## Air cooled HX calculator
FOR EDUCATIONAL PURPOSE ONLY – DO NOT USE THIS METHOD FOR DETAIL DESIGN – ALWAYS CONSULT A REPUTABLE SUPPLIER FOR DETAIL DESIGN
Air cooled Heat Exchanger Design Calculator (estimation)
| To modify | Calculated
Step 1 : Assume the heat exchanger geometry
Please refer to the sheet heat exchanger geometry
Choose a density for the fins and a pitch, and a number of row
|  |  | Number of rows of the exchanger | Nr | 5
|  |  | Fins density |  | 10 | fins/in
|  |  | Tube spacing |  | 2.5 | in
|  |  | Face velocity | FV | 625
Step 2 : Gather the data required for the design
Process data
|  |  | Type of heat exchanger |  | Air cooled
|  |  | Air ambient temperature | T1 | 35 | c
|  |  | Hot Fluid to cool |  | Water
|  |  | Hot fluid flowrate | w | 500000 | lb/h
|  |  | Hot fluid specific heat | c | 1 | Btu
|  |  | Hot fluid inlet temperature | t1 | 150 | c
|  |  | Hot fluid outlet temperature | t2 | 50 | c
Heat exchanger basic data
|  |  | Tube material |  | Steel + Al fins
|  |  | Tube thermal conductivity | λm | 25 | Btu/h.ft2.F
|  |  | Tube inside diameter | Di | 0.834 | in
|  |  | Tube outside diameter | Do | 1 | in
|  |  | Heat transfer coefficient on the hot fluid side | hi | 1000 | Btu/h.ft2.F
|  |  | Fouling Heat transfer coefficient on the hot fluid side | hs | 1000 | Btu/h.ft2.F
Step 3 Calculate the air side heat transfer coefficient
|  |  | Air side heat transfer coefficient | ha | 200 | Btu/h.ft2.F
Step 4 : Calculate the conduction coefficient through the tube
|  |  | Heat transfer coefficient through the tube wall | hw | 3614.4578 | Btu/h.ft2.F
(Note that the diameters in inches are converted in ft in the formula)
Step 5 : Calculate the overall heat transfer coefficient
|  |  | Overall heat transfer coefficient | U | 133.7666 | Btu/h.ft2.F
Step 6 : Estimate air outlet temperature
Please refer to the sheet air outlet temperature estimation
Considering the overall heat transfer coefficient and the hot fluid inlet temperature
|  |  | Air outlet temperature estimation | T2 | 83 | c
Step 7 : Calculate the heat exchanger size
|  |  | Tubes length | L | 40 | ft
|  |  | Required heat duty of the exchanger | Q | 90000000 | Btu/h
|  |  | Face area of the exchanger | FA | 1538.4615 | ft2
|  |  | Heat exchanger width | Y | 38.4615 | ft
Step 8 : Calculate available area and check it is sufficient
|  |  | Select a bundle width |  | 120 | in | Must change by 6 in increments, minimum 48 in, maximum 144 in
|  |  | Required number of bundles |  | 3.8462
|  |  | Selected number of bundles | Nb | 4 |  | Round the value calculated above
|  |  | Designed Heat exchanger width | Y | 39.9998 | ft
|  |  | Number of tubes per row | Nt | 191
|  |  | Calculated air outlet temperature | T2 | 81.154 | c
|  |  | Calculated DTML | DTML | 35.3361 | c
|  |  | Required heat exchange area | A required | 10577.991 | ft2
|  |  | Available exchange area | A available | 10000.7366 | ft2
|  |  | Available > Required ? |  | Design not ok, change bundle width
if yes, the design is acceptable, if not come back to the bundle width and adjust
Step 9 : calculate the air side pressure drop and fan power requirement
|  |  | Air pressure drop | Dpa | 0.50091 | inches W
|  |  | Required fan power | bhp | 185.0541 | bhp
If you spot a mistake or wish to suggest an improvement, please contact : contact@myengineeringtools.com
Copyright www.MyEngineeringTools.com
The content of MyEngineeringTools.com is copyrighted but no warranty nor liability is ensured. The content of this site is to be seen as a help and important information and calculation must always be double checked by the user through the quality procedure of his organization or by checking another source. The user must always respect all applicable regulation. The use of the information is at the user and its organization own risk and own cost.
FOR EDUCATIONAL PURPOSE ONLY – DO NOT USE THIS METHOD FOR DETAIL DESIGN – ALWAYS CONSULT A REPUTABLE SUPPLIER FOR DETAIL DESIGN

## Heat exchanger geometry
Face velocity
| 8 fins / inch (315 fins / m) 2.375 inch pitch (0.0603 m) |  | 10 fins / inch (394 fins / m) 2.375 inch pitch (0.0603 m) |  | 10 fins / inch (394 fins / m) 2.5 inch pitch (0.0635 m)
Number of rows | ft/min | m/s | ft/min | m/s | ft/min | m/s
3 | 650 | 3.3 | 625 | 3.18 | 700 | 3.56
4 | 615 | 3.12 | 600 | 3.05 | 660 | 3.35
5 | 585 | 2.97 | 575 | 2.92 | 625 | 3.18
6 | 560 | 2.84 | 550 | 2.79 | 600 | 3.05

## Air outlet temperature estimate
Outlet air temperature, c
Process inlet temperature, c | U=50 | U=100 | U=150
| (BTU/h.ft2.F) | (BTU/h.ft2.F) | (BTU/h.ft2.F)
175 | 90 | 95 | 100
150 | 75 | 80 | 85
125 | 70 | 75 | 80
100 | 60 | 65 | 70
90 | 55 | 60 | 65
80 | 50 | 55 | 60
70 | 48 | 50 | 55
60 | 45 | 48 | 50
50 | 40 | 41 | 42