## Field Estimation
FOR EDUCATIONAL PURPOSE ONLY – DO NOT USE THIS METHOD FOR DETAIL DESIGN – ALWAYS CONSULT A REPUTABLE SUPPLIER FOR DETAIL DESIGN
Centrifugal Pump Shut-Off Head Calculator
| To modify | Calculated
Sheet 1: Field Estimation
| Parameter | Value | Unit | Result | Formula
| Impeller Diameter (D) | 0.3 | meters
| Rotational Speed (N) | 1500 | RPM
| Empirical Factor (k) | 150 | -
| Estimated Shut-Off Head |  | meters | 30.375 | H = k × (D²) × (N/1000)²
K-Factor Guidelines
Typical Range: 100-200
Important Notes:
• K-factor varies based on specific speed (Ns)
• Depends on hydraulic design
• Not constant across pump designs
• Consult manufacturer data
⚠️ WARNING: This is a rough estimation
Never replace manufacturer certified curves
If you spot a mistake or wish to suggest an improvement, please contact : contact@myengineeringtools.com
Copyright www.MyEngineeringTools.com
The content of MyEngineeringTools.com is copyrighted but no warranty nor liability is ensured. The content of this site is to be seen as a help and important information and calculation must always be double checked by the user through the quality procedure of his organization or by checking another source. The user must always respect all applicable regulation. The use of the information is at the user and its organization own risk and own cost.
FOR EDUCATIONAL PURPOSE ONLY – DO NOT USE THIS METHOD FOR DETAIL DESIGN – ALWAYS CONSULT A REPUTABLE SUPPLIER FOR DETAIL DESIGN

## Thermal Safety
FOR EDUCATIONAL PURPOSE ONLY – DO NOT USE THIS METHOD FOR DETAIL DESIGN – ALWAYS CONSULT A REPUTABLE SUPPLIER FOR DETAIL DESIGN
Thermal Safety Analysis
| To modify | Calculated
| Parameter | Value | Unit | Result | Formula
| Brake HP at Shut-Off (P) | 75000 | Watts
| Mass of Trapped Fluid (m) | 150 | kg
| Specific Heat (cp) | 4186 | J/kg·°C
| Max Temperature Rise (ΔT) | 40 | °C
| Safe Operation Time |  | minutes | 5.5813 | t = (ΔT_max × m × cp) / P
Fluid Properties Reference
| Fluid | Cp (J/kg·°C) | Density (kg/m³)
| Water | 4186 | 1000
| Light Oil | 2100 | 850
| Heavy Oil | 1900 | 950
| Glycol | 2400 | 1100
| Diesel | 2200 | 840
💡 Note: Use BHP at shut-off from pump curve
NOT motor nameplate power
BHP at shut-off is typically 40-60% of motor power
If you spot a mistake or wish to suggest an improvement, please contact : contact@myengineeringtools.com
Copyright www.MyEngineeringTools.com
The content of MyEngineeringTools.com is copyrighted but no warranty nor liability is ensured. The content of this site is to be seen as a help and important information and calculation must always be double checked by the user through the quality procedure of his organization or by checking another source. The user must always respect all applicable regulation. The use of the information is at the user and its organization own risk and own cost.
FOR EDUCATIONAL PURPOSE ONLY – DO NOT USE THIS METHOD FOR DETAIL DESIGN – ALWAYS CONSULT A REPUTABLE SUPPLIER FOR DETAIL DESIGN

## Operation Analysis
FOR EDUCATIONAL PURPOSE ONLY – DO NOT USE THIS METHOD FOR DETAIL DESIGN – ALWAYS CONSULT A REPUTABLE SUPPLIER FOR DETAIL DESIGN
Operating Condition Analysis
| To modify | Calculated
| Parameter | Value | Unit | Result | Analysis
| Estimated Shut-Off Head | 30.4 | meters
| Actual Operating Head | 28 | meters
| Best Efficiency Point Head | 25 | meters
Performance Metrics
| Distance from Shut-Off |  | meters | 2.4
| Distance from BEP |  | meters | 3
| Operating Ratio (Actual/Shut-Off) |  |  | 0.92105
| Operating Status |  |  | CRITICAL: Too close to shut-off
Recommendations
• Monitor pump vibration and temperature
• Install minimum flow bypass for critical apps
• Verify with manufacturer pump curves
If you spot a mistake or wish to suggest an improvement, please contact : contact@myengineeringtools.com
Copyright www.MyEngineeringTools.com
The content of MyEngineeringTools.com is copyrighted but no warranty nor liability is ensured. The content of this site is to be seen as a help and important information and calculation must always be double checked by the user through the quality procedure of his organization or by checking another source. The user must always respect all applicable regulation. The use of the information is at the user and its organization own risk and own cost.
FOR EDUCATIONAL PURPOSE ONLY – DO NOT USE THIS METHOD FOR DETAIL DESIGN – ALWAYS CONSULT A REPUTABLE SUPPLIER FOR DETAIL DESIGN

## Reference Tables
Reference Tables and Safety Guidelines
Critical Operating Zones
Zone | Flow Range | Risk Level
Shut-Off | 0-5% of rated | Critical
Unstable | 5-25% of rated | High
Stable | 25-120% of rated | Low
End of Curve | 120%+ of rated | Medium
Typical BHP at Shut-Off
Motor Size | BHP at Shut-Off
50 HP Motor | 20-30 kW
100 HP Motor | 40-60 kW
200 HP Motor | 75-110 kW
500 HP Motor | 180-270 kW
🔴 CRITICAL SAFETY NOTES:
• Always verify with manufacturer curves
• Never exceed calculated safe operation time
• Install minimum flow bypass for critical apps
• Monitor pump vibration and temperature
• Conduct Factory Acceptance Testing (FAT)