## Simple pipe
FOR EDUCATIONAL PURPOSE ONLY – DO NOT USE THIS METHOD FOR DETAIL DESIGN – ALWAYS CONSULT A REPUTABLE SUPPLIER FOR DETAIL DESIGN
Calculation Tool Heat loss of an insulated pipe
Temperature of pipe and air
| Skin temperature pipe | Ts | ºc | 160 | ºR | 779.67
| Air temperature | Ta | ºc | 20 | ºR | 527.67
Atmospheric conditions
| Wind speed | v | km/h | 10 | ft/h | 32808.4
| Specific heat of air | c | J/kg.c | 1005 | BTU/lb/F | 0.24004
| Density of air | ρ | kg/m3 | 1.22 | lb/ft3 | 0.076165
Pipe characteristics
| Material | - | - | Carbon steel
| Material conductivity | λ1 | W/m/K | 142 | BTU/h.ft.F | 82.076
| Insulating material conductivity | λ2 | W/m/K | 0.285 | BTU/h.ft.F | 0.16473
| Tube inside diameter | Di | mm | 60 | ft | 0.19685
| Tube oulet diameter | D | mm | 66 | ft | 0.21654
| Outside diameter with insulation | Do | mm | 106 | ft | 0.34777
| Pipe length | L | m | 10 | ft | 32.8084
| Pipe external surface | A | m2 | 3.3301 | ft2 | 35.8451
Heat transfer coefficient on the inside of the pipe
| Heat transfer coefficient in pipe | hi | W/m2/c | 8517.395 | BTU/h.ft2.F | 1500
Heat loss through radiation
| Heat loss through radiation | hr | W/m2/c | 5.6783 | BTU/h.ft2.F | 1
Heat loss through convection
| Mass velocity of air | G | kg/h.m2 | 12200 | lb/h.ft2 | 2498.8387
| Heat transfer coefficient | hc | W/m2/c | 25.0045 | BTU/h.ft2.F | 4.4036
Total pipe heat loss
| Outside heat transfer coefficient | h | W/m2/c | 30.6828 | BTU/h.ft2.F | 5.4036 | Intermediary calculations
| Overal heat transfer coefficient | U | W/m2/c | 8.2706 | BTU/h.ft2.F | 1.4565 | 0.0011778 | 0.00020192 | 0.50011 | 0.18506
| Total pipe heat loss | Q total | kW | 3.8559 | BTU/h | 13156.8923
| If you spot a mistake please contact : |  | mailto:contact@myengineeringtools.com
Copyright www.PowderProcess.net
The content of PowderProcess.net is copyrighted but no warranty nor liability is ensured. The content of this site is to be seen as a help and important information and calculation must always be double checked by the user through the quality procedure of his organization or by checking another source. The user must always respect all applicable regulation. The use of the information is at the user and its organization own risk and own cost.
FOR EDUCATIONAL PURPOSE ONLY – DO NOT USE THIS METHOD FOR DETAIL DESIGN – ALWAYS CONSULT A REPUTABLE SUPPLIER FOR DETAIL DESIGN